- Module 6

Fire Design

Lecture 16:Introduction to fire design according to Eurocode 3

- Contents:

1.	Construction materials at high temperatures

1.1.	Steel

1.2.	Concrete

2.	Temperatures in fires

3.	Behaviour of beams and columns in furnace tests

4.	Fire protection methods

5.	Simple Eurocode design of steel members

5.1.	Loadings

5.2.	Basic principles of fire resistant design

6.	Material properties

6.1.	Steel strengths

6.2.	Concrete strengths

6.3.	Thermal expansion of steel and concrete

6.4.	Other relevant thermal properties of steel

7.	Section classification

8.	Critical temperature

9.	Resistance of tension members

10.	Resistance of beams

11.	Lateral-torsional buckling

12.	Resistance of compression members

13.	Fire resistance time of unprotected steel members

14.	Fire resistance times of protected steel members

15.	Use of advanced calculation models

16.	Eurocode simple fire resistance calculation examples

16.1.	Design example

16.2.	Fire Resistance and Protection of a Tension Member

16.2.1.	Ambient temperature design of BE

16.2.2.	Fire resistance of tension member BE

16.2.3.	Fire protection of tension member BE

16.3.	Fire Resistance and Protection of a Steel Beam

16.3.1.	Ambient temperature design of minor beam AB

16.3.2.	Fire resistance of minor beam AB

16.3.3.	Fire protection of minor beam AB

16.4.	Fire Resistance and Protection of a Steel Column

16.4.1.	Ambient temperature design of column GH

16.4.2.	Fire resistance of steel column GH

17.	References

| - Construction materials at high temperatures |  |
| --- | --- |
| - Steel |  |
| Most construction materials suffer a progressive loss of strength and stiffness as their temperature increases. For steel the change can be seen in Eurocode 3 stress-strain curves (Figure 1) at temperatures as low as 200°C. Although melting does not happen until about 1500°C, only 23% of the ambient-temperature strength remains at 700°C. At 800°C this has reduced to 11% and at 900°C to 6%. | Part 1-2 3.2 Table 3.1 Fig. 3.1 |
| - Modifications of stress-strain relationships with temperature for S275 steel (Eurocode 3 curves). |  |
| - Concrete |  |
| Concrete also loses strength properties as its temperature increases (Figure 2). | EC4 Part 1-2 |
| - Eurocode 4 stress-strain- temperature curves for calcareous concrete |  |
| Concrete has a lower thermal conductivity than steel and is therefore a relatively good insulator to reinforcement or embedded parts of sections. Fire resistance of reinforced concrete members tends to be based on the strength reduction of reinforcement which is largely controlled by the cover specification. However, concrete is affected by spalling, which is a progressive breaking away of concrete from the fire-exposed surface where temperature variation is high, and this can lead to the exposure of reinforcement as a fire progresses. Its behaviour at elevated temperatures depends largely on the aggregate type used; siliceous (gravel, granite) aggregate tends to cause concrete to spall more readily than calcareous (limestone) aggregate. High strength concrete are more prone to spalling, presumably because of their lower gas permeability. Lightweight concrete possesses greater insulating properties than normal-weight concrete. |  |
| - Temperatures in fires |  |
| A real fire in a building grows and decays in accordance with the mass and energy balance within the compartment in which it occurs (Figure 3). The energy released depends upon the quantity and type of fuel available. The rate at which the energy is released depends upon the ventilation conditions and type of fuel. |  |
| - Phases of a natural fire, comparing atmosphere temperatures with the ISO834 standard fire curve |  |
| It is possible to consider a real fire as consisting of three phases, which may be defined as growth, full development and decay. The most rapid temperature rise occurs in the period of flashover, which is the point at which all organic materials in the compartment spontaneously combust. |  |
| Fire resistance times specified in most national building regulations relate to heating according to an internationally agreed time-temperature curve defined in ISO834 (or Eurocode 1 Part 1-2), which does not represent any type of natural building fire. It is characterised by an atmosphere temperature which rises continuously with time, but at a diminishing rate (Figure 4). This standard design curve is systematically used in furnace testing of components. The quoted value of fire resistance time does not therefore indicate the actual time for which a component will survive in a building fire, but should be used for rating different structural systems against each other. |  |
| The proposed “external fire curve” is not to be used for cases where the structure for which the fire resistance is being considered as external, but when the external façade of a building is subjected to a fire from another building. |  |
| - Atmosphere temperature for ISO834 standard fire |  |
| In cases where storage of hydrocarbon materials makes fires extremely severe a “Hydrocarbon Fire” curve is also given. These three “Nominal” fire curves are shown in Figure 5. | EC1 Part 1-2 3.2 |
| - Eurocode 1 Part 1-2 nominal fire curves compared with a parametric fire |  |
| Any of the normal means of establishing fire resistance times (tabulated data or calculation models) may be used against these curves. |  |
| An alternative method to the use of nominal fire curves, which may only be used directly with fire resistance calculation models, is to attempt to model a natural fire using a “parametric” fire curve for which equations are provided in Eurocode 1 Part 1-2. This enables fairly simple modelling of fire temperatures evolution in the heating and cooling phases of the post-flashover fire (the initial growth phase is not addressed). It is necessary to have data on the properties (density, specific heat, thermal conductivity) of the materials enclosing a compartment, the fire load (fuel) density and ventilation areas when using these equations. They are limited in application to compartments of up to floor area of 500 m2, floor to ceiling distance up to 4 m and no opening in the ceiling, with mainly cellulosic (paper, wood, etc.) fire loads. | EC1 Part 1-2 Annex A, E |
| It may be advantageous to the designer to use parametric curves in cases where the density of combustible materials is low, where using the nominal fire curves is unnecessarily conservative. |  |
| Another concept known as ‘equivalent time’ can also be used both to relate the resistance times of structural elements in a real fire to their resistance in the standard fire. The principle is shown in Figure 6. This concept can only be applied where the behaviour of the structure is dictated by a single temperature such as the supposedly uniform temperature of a steel member. The application is more questionable in composite structures where the temperature field is highly non uniform. | EC1 Part 1-2 Annex F |
| - Time-equivalent severity of natural fires |  |
| This is useful in applying calculation models which are based on the standard fire heating curve, but the important aspect of using parametric fire curves and the calculated structure temperatures which come from these is that they represent an absolute test of structural fire resistance by comparing the maximum temperature reached by the structure against its critical temperature, rather than an assessment of the way it would perform if it were possible to subject it to a standard fire time-temperature curve based on furnace testing. |  |
| - Behaviour of beams and columns in furnace tests |  |
| Furnace testing using the standard time-temperature atmosphere curve was historically the traditional means of assessing the behaviour of frame elements in fire, but the difficulties of conducting furnace tests of representative full-scale structural members under load are obvious. The size of furnaces limits the size of the members tested, usually to less than 5 m, and if a range of load levels is required then a separate specimen is required for each of these. Tests on small members may be unrepresentative of the behaviour of larger members. |  |
| A further serious problem with the use of furnace tests in relation to the behaviour of similar elements in structural frames is that the only clearly defined and reliable support condition for a member in a furnace test is simply supported, with the member free to expand axially. When a member forms part of a fire compartment surrounded by adjacent structure which is unaffected by the fire its thermal expansion is resisted by restraint from this surrounding structure. |  |
| This is a problem which is unique to the fire state, because at ambient temperatures structural deflections are so small that axial restraint is very rarely an issue of significance. Axial restraint can in fact work in different ways at different stages of a fire; in the early stages the restrained thermal expansion dominates, and very high compressive stresses are generated, but in the later stages when the weakening of the material is very high the restraint may begin to support the member by resisting pull-in. Furnace tests which allow axial movement cannot reproduce these restraint conditions at all; in particular, in the later stages a complete collapse would be observed unless a safety cut-off criterion is applied. In fact a beam furnace test is always terminated at a deflection of not more than span / 20 for exactly this reason. |  |
| When an element is part of a structural frame, not only restraint to axial expansion, but also rotational restraint may be present at the ends of the element. This restraint is also changing during the course of the fire. Rotational restraint is usually not applied during a furnace test on single elements. |  |
| Only recently has any significant number of fire tests been performed on fire compartments within whole structures. Some years may pass before these full-scale tests are seen to have a real impact on design codes. In fact full-scale testing is so expensive that there will probably never be a large volume of documented results from such tests, and those that exist will have the major function of being used to validate numerical models on which future developments of design rules will be based. The basic design procedures of Eurocode 3 and 4 for use in routine fire engineering design are still in terms of isolated members for which fire resistance is considered mainly in terms of a real or simulated furnace test. Yet, Eurocodes 3 and 4 allow for the use of advanced calculation models, and these are more and more often used, at least in projects of a certain size and complexity. |  |
| - Fire protection methods |  |
| The traditional approach to fire resistance of steel structures has been to clad the members with insulating material. This may be in alternative forms: |  |
| - Boarding (plasterboard or more specialised systems based on mineral fibre or vermiculite) fixed around the exposed parts of the steel members. This is fairly easy to apply and creates an external profile which is aesthetically acceptable, but is inflexible in use around complex details such as connections. Ceramic fibre blanket may be used as a more flexible insulating barrier in some cases; - Sprays which build up a coating of prescribed thickness around the members. These tend to use vermiculite or mineral fibre in a cement or gypsum binder. Application on site is fairly rapid, and does not suffer the problems of rigid boarding around complex structural details. Since the finish produced tends to be unacceptable in public areas of buildings these systems tend to be used in areas which are normally hidden from view, such as beams and connections above suspended ceilings; - Intumescing paints, which provide a decorative finish under normal conditions, but which foam and swell when heated, producing an insulating char layer which is up to 50 times as thick as the original paint film. They are applied by brush, spray or roller, and must achieve a specified thickness which may require several coats of paint and measurement of the film thickness. |  |
| All of these methods are normally applied as a site operation after the main structural elements are erected. This can introduce a significant delay into the construction process, which increases the cost of construction to the client. The only exception to this is that some systems have recently been developed in which intumescents are applied to steelwork at the fabrication stage, so that much of the site-work is avoided. However, in such systems there is clearly a need for a much higher degree than usual of resistance to impact or abrasion. |  |
| These methods can provide any required degree of protection against fire heating of steelwork, and can be used as part of a fire engineering approach. However traditionally thicknesses of the protection layers have been based on manufacturers’ data aimed at the relatively simplistic criterion of limiting the steel temperature to less than 550°C at the required time of fire resistance in the ISO834 standard fire. In some cases, material properties for design are determined from the results by semi-empirical means. |  |
| Full or partial encasement of open steel sections in concrete is occasionally used as a method of fire protection, particularly in the case of columns for which the strength of the concrete, either reinforced or plain, can contribute to the ambient-temperature strength. In the case of hollow steel sections concrete may be used to fill the section, again either with or without reinforcing bars. In fire this concrete acts to some extent as a heat-sink, which slows the heating process in the steel section. For significant fire durations, this effect is not maintained because the temperature of the external steel tube tends toward the temperature of the hot gases; the system finally behaves as a reinforced concrete column with the steel tube having lost nearly all load bearing capacity. The positive effect that remains is that no part of concrete can leave the tube as a result of progressive spalling, whereas this is often observed in usual concrete columns. In a few buildings hollow-section columns have been linked together as a system and filled with water fed from a gravity reservoir. This can clearly dissipate huge amounts of heat, but at rather high cost, both in construction and maintenance. |  |
| The most recent design codes are explicit about the fact that the structural fire resistance of a member is dependent to a large extent on its loading level in fire (and also that loading in the fire situation has a very high probability of being considerably less than the factored loads for which strength design is performed). This presents designers with another option which may be used alone or in combination with other measures. A reduction in load level by selecting steel members which are stronger than is needed for ambient temperature strength, possibly as part of a strategy of standardising sections, can enhance the fire resistance times. This can allow unprotected elements to be used, at least for a duration of standard fire up to 30 minutes. |  |
| Alternative fire engineering strategies are beyond the scope of this lecture, but there is an active encouragement to designers in the Eurocodes to use agreed and validated advanced calculation models for the behaviour of the whole structure or sub-assemblies. The clear implication of this is that designs which can be shown to gain fire resistance overall by providing alternative load paths when members in a fire compartment have individually lost all effective load resistance are perfectly valid under the provisions of these codes. This is a major departure from the traditional approach based on the fire resistance of each component. In its preamble Eurocode 3 Part 1-2 also encourages the use of integrated fire strategies, including the use of combinations of active (sprinklers) and passive protection. A method is provided in Eurocode 1 Part 1-2 that allows a reduction of the design value of the fire load depending on the active protection measures, but this applicability of this method is a matter for national Building Regulations through the National Application Document that each Member State has to produce. | EC1, Part 1-2, Annex E |
| - Simple Eurocode design of steel members |  |
| Example design calculation using Eurocode 3 simple calculation models are given later, and so this section concentrates on the principles of these methods rather than their detail. |  |
| Eurocodes use a very systematic notation in which different symbols are used for general and particular versions of parameters. For example an “effect of an action” is denoted in general terms as E in establishing a principle; in particular members this might become the axial force N or the internal bending moment M. Subscripts denoting different attributes of a parameter may be grouped, using dots as separators, as in Efi.d.t which denotes the design value of the effect of an action in fire, at the required time of resistance. Commonly used notations in the fire engineering parts of Eurocodes 1, 3 and 4 are: |  |
| E effect of actions G permanent action Q variable action Rfi load-bearing resistance tfi standard fire resistance time of a member tfi,requ standard fire resistance time nominal requirement  temperature cr critical temperature of a member  partial safety factor  load combination factor | Part 1-2 1.6 |
| and the following subscript indices may be used alone or in combination: |  |
| A accidental design situation cr critical value fi relevant to fire design d design value  associated with certain temperature (may be replaced by value) k characteristic value t at certain fire exposure time (may be replaced by value) 1, 2 ... ranking order for frequency of variable actions |  |
| - Loadings |  |
| Eurocode 1 Part 1-2 presents rules for calculating design actions (loadings) in fire, which recognise the low probability of a major fire occurring simultaneously with high load intensities. The normal Eurocode classification of loads is as permanent and variable; in fire the characteristic permanent actions (dead loading) are used unfactored (GA = 1,0) while the principal characteristic variable action (imposed loading) is factored down by a combination factor fi that is taken either for quasi permanent value 2,1 or for frequent value1,1, to be chosen in the N.A.D. by each member state, and whose value is between 0,2 and 0,9 depending on the type of loading (wind, snow, live load) and building usage. | EC1 Part 1-2 4.3.1 |
| Where indirect fire actions, i.e. effects of thermal expansion, need not be explicitly considered, effects of actions may be determined by analysing the structure for combined actions for t = 0 only and these effects are taken as constant throughout fire exposure. | EC1 Part 1-2 4.3.2 |
| As a further simplification, the design effect of actions during the fire Efi,d can be calculated from those determined in normal temperature design on the base of the factored design loads: |  |
|  | Part 1-2 2.4.2 (3) |
| For steel members ,this factor fi may be expressed in terms of the characteristic loads and their factors when only the principal variable action is used together with the permanent action as: | EC4 part 1-2 2.4.2 (2) |
| Typical values of the safety factors specified in Eurocode 1 are: |  |
| GA = 1,0 (Permanent loads: accidental design situations) fi = 2,1 = 0,3 (Combination factor: variable loads, office buildings) G = 1,35 (Permanent loads: strength design) Q,1 = 1,5 (Variable loads: strength design) |  |
| - Basic principles of fire resistant design |  |
| Structural fire-resistant design of a member is concerned with establishing that it satisfies the requirements of national building regulations over the designated time period when subjected to the appropriate fire curve. This can be expressed in three alternative ways: |  |
| - The fire resistance time should exceed the requirement for the building usage and type when loaded to the design load level and subjected to the fire temperature curve: | EC1 Part 1-2 2.5 |
| tfi,d≥tfi,requ |  |
| - The load-bearing resistance of the element should exceed the design loading at any time during the fire and until when it has been heated for the required time in the fire: |  |
| Rfi,d,t≥Efi,d,t |  |
| - The critical temperature of an element loaded to the design level should exceed the design temperature at any time during the fire and until the required time (this approach is only possible when the behaviour of the member is governed by one single representative temperature as is the case, for example, for steel members at uniform temperature): |  |
| θcr,d≥θd |  |
| - Material properties |  |
| - Steel strengths |  |
| A set of stress-strain curves for S275 steel has already been shown in Figure 1 as an example of the principal effect of temperature in weakening steels. | Part 1-2 Fig. 3.2 |
| - Eurocode 3 Strength reduction for structural steel (SS) and cold-worked reinforcement (Rft) at high temperatures | EC4 Part 1-2 |
| These are based on an extensive series of tests, which have been modelled by equations representing an initial linear elastic portion, changing tangentially to a part-ellipse whose gradient is zero at 2% strain. When curves such as these are presented in normalised fashion, with stresses shown as a proportion of ambient-temperature yield strength, the curves at the same temperatures for S235, S275, S355, S420 and S460 steels of EN 10025 and all steel grades defined in EN 10210 and EN 10219 are extremely close to one another. It is therefore possible to use a single set of strength reduction factors (Figure 7) for all three grades, at given temperatures and strain levels. In Eurocodes 3 and 4 strengths corresponding to 2% strain are used in the fire engineering design of all types of structural members. |  |
| Hot-rolled reinforcing bars are treated in Eurocode 4 in similar fashion to structural steels, but cold-worked reinforcing steel, whose standard grade is S500, deteriorates more rapidly at elevated temperatures than do the standard grades. Its strength reduction factors for effective yield and elastic modulus are also shown on Figure 7. |  |
| - Concrete strengths |  |
| The stress-strain curves at different temperatures for concrete have a significant difference in form from those for steel. The curves all have a maximum compressive strength, rather than an effective yield strength, which occurs at strains which progressively increase with temperature, followed by a descending branch. Tensile strength for all concretes is normally considered to be zero. As is normal in Eurocodes, alternative material constitutive laws may be used provided that they are supported by experimental evidence. |  |
| For normal-weight concretes (density around 2400 kg/m3) only the lower range of strength values, corresponding to the siliceous type which is shown in Figure 8, are tabulated in Eurocode 4 Part 1-2. For calcareous-aggregate concrete these are also used, being inherently conservative values. Where more detail is required designers are referred to Eurocode 2 Part 1-2. |  |
| - Eurocode 4 strength reduction for normal-weight siliceous concrete and lightweight concrete at elevated temperatures | EC4 Part 1-2 |
| Lightweight concretes are defined as those within the density range 1600-2000 kg/m3. Although in practice they may be created using different forms of aggregate, they are treated in Eurocode 4 Part 1-2 as if they degrade similarly with temperature. Hence the single set of strength reduction factors (Figure 8) for lightweight concrete is again on the conservative side. |  |
| - Thermal expansion of steel and concrete |  |
| In most simple fire engineering calculations on simple elements exposed to the standard fire, thermal expansion of materials is neglected. When larger structures are considered and more advanced calculation models are used, it is necessary to recognise that thermal expansion in the structure around the fire compartment is resisted by the cool structure outside this zone, and that this causes behaviour which is considerably different from that experienced by similar members in an unrestrained situation. It is therefore necessary at least to appreciate the way in which the thermal expansion coefficients of steel and concrete vary with temperature. They are shown in Figure 9; perhaps the most significant aspect to note is that the thermal expansion coefficients of steel and concrete are of comparable magnitudes in the practical range of fire temperatures. |  |
| - Variation of Eurocode 3/4 thermal expansion coefficients of steel and concrete with temperature. | Part 1-2 3.4.1.1 EC4 Part 1-2 3.3 |
| It can be observed that, according to the recommended values, thermal expansion of concrete ceases altogether at 700°C, whereas in steel a crystal-structure change takes place between 750°C and 860°C and the thermal expansion temporarily stops. |  |
| - Other relevant thermal properties of steel |  |
| Two additional thermal properties of steel affect its heating rate in fire. |  |
| Thermal conductivity has a rather low influence on the heating rate of steel members because they are normally made of thin plates. A simplified version of the change of conductivity with temperature, defined in Eurocode 3, is shown in Figure 10. |  |
| The specific heat of steel is the amount of heat which is necessary to raise the steel temperature by 1°C. This varies to some extent with temperature across most of the range, as is shown in Figure 11, but its value undergoes a very dramatic change in the range 700-800°C. The apparent sharp rise to an very high value at about 735°C is actually an indication of the latent heat input needed to allow the crystal-structure phase change to take place. |  |
| - Eurocode 3 representations of the variation of thermal conductivity of steel with temperature | Part 1-2 3.4.1.3 |
| - Variation of the specific heat of steel with temperature | Part 1-2 3.4.1.2 |
| - Section classification |  |
| It is essential for both the ambient-temperature and fire design of all members which act wholly or partly in compression that they are classified in order to establish the appropriate design calculation methods to be used. This is basically a check on the slenderness of the parts of the cross-section which act in compression in order to assess their vulnerability to local buckling. This applies just as much in fire as in normal design, since the strain levels in fire are liable to become very high, and since strengths are reduced in fire these elevated-temperature material properties should be used when performing a section classification. It is worth re-stating briefly the definitions of the four possible classes of member: |  |
| - Class 1 sections: stocky cross-sections which can be used reliably in plastic strength calculations because they can develop plastic bending moment capacity with a sufficient capacity of rotation; - Class 2 sections: whilst the member resistance may be calculated on the basis of its plastic capacity, it is not capable of sufficient extra rotation without the occurrence of local buckling to allow other hinges to form as part of a fully developed mechanism. The frame should therefore be designed elastically but based on plastic moment capacity in the sections; - Class 3 sections: the member resistance should be calculated elastically at its initial yield capacity; - Class 4 sections: slender cross-sections whose resistance is governed by elastic local buckling below the yield strength of the material. |  |
| In fire design members are classified as for ambient temperature design, but with a reduced value of  equal to: |  |
|  | Part 1-2 4.2.2 |
| This account for the fact that the Young's modulus exhibits a faster reduction with temperature than the effective yield strength. |  |
| - Critical temperature |  |
| The critical temperature cr of a member is the temperature at which the member is calculated to fail under its given loading. This can be determined when using Eurocode 3 for members in which instability is not involved in the failure mode from the degree of utilisation 0 of the member in the fire design situation. |  |
| - Critical temperature, related to degree of utilisation | Part 1-2 4.2.4 |
| The following equation, plotted in Figure 12, defines the critical temperature: |  |
|  | Part 1-2 4.2.4 |
| This equation is in fact an approximate best fit equation to this invert of the effective yield strength of carbon steel as a function of the temperature. For the very slender Class 4 sections, a single conservative critical temperature of 350°C is specified. The critical temperature of Class 4 sections may be calculated and found higher than 350°C if calculated according to Annex E of Eurocode 3 Part 1-2. | Part 1-2 4.2.3.6 |
| The degree of utilisation 0 is basically the design loading in fire as a proportion of the design resistance, where the latter is calculated at ambient temperature (or at time t = 0) but using the material partial safety factors which apply in fire design rather than in normal strength design: |  |
| A simple conservative version, which can be used for elements where instability is not a possibility, is |  |
| in which the reduction factor fi may already be conservative. |  |
| - Resistance of tension members |  |
| For a tension member under uniform cross-sectional temperature  the design resistance in fire is calculated simply by using the reduction factor ky, on yield strength at elevated temperature, with an adjustment for the relative material safety factors in normal design and fire design: | Part 1-2 4.2.3.1 |
| so that the degree of utilisation is simply: |  |
| - Resistance of beams |  |
| Moment resistance in fire for Class 1 or 2 sections with uniform cross-sectional temperature  is again calculated from the normal plastic resistance moment for strength design, simply by using the reduction factor ky, on yield strength at elevated temperature, with an adjustment for the relative material safety factors in normal design and fire design: | 4.2.3.3 |
| For a Class 3 section the same expression applies, but with the elastic moment of resistance used for MRd. | 4.2.3.4 |
| In the case of beams supporting concrete slabs on the top flange the non-uniform temperature distributions may be accounted for analytically in calculating the design moment resistance, by dividing the cross-section into uniform-temperature elements, reducing the strength of each according to its temperature, and finding the resistance moment by summation across the section. Alternatively it may be dealt with conservatively by the use of two empirical adaptation factors 1 and 2 to define the moment resistance at time t as: |  |
| where 1 is the factor for non-uniform cross-sectional temperature and 2 is the factor for temperature reduction towards the supports of a statically indeterminate beam. The actual values of 1 and 2 are specified in National Application Documents. Many countries are using values of 1 higher than the value of 0,7 recommended in the Eurocode because this value was based on experimental test results made in the UK in which some kind of connection was present between the steel profiles and the supposedly non collaborating concrete slabs. |  |
| Shear resistance is determined using the same general process as for bending and tension resistance, with the same adaptation factors as those above in cases with non-uniform temperature distribution. The general expression, covering uniform and non-uniform temperature cases, is: |  |
| - Lateral-torsional buckling |  |
| In cases where the compression flange is not continuously restrained the design resistance moment against lateral-torsional buckling is calculated for Class 1 or 2 sections using the formula from Eurocode 3 Part 1-1, with minor amendment for the fire state: | 4.2.3.3 |
| with: |  |
| LT,fi lateral-torsional buckling reduction factor in fire design situation ky,com yield strength reduction factor at the maximum compression flange temperature at time t |  |
| The lateral-torsional buckling reduction factor LT is determined with a special instability curve for the fire situation, with the normalised slenderness adapted to the high-temperature steel properties: |  |
| with: |  |
| kE,,com elastic modulus reduction factor at the maximum compression flange temperature at time t |  |
| - Resistance of compression members |  |
| The design buckling resistance of columns of Class 1, 2 or 3 is calculated as follows, allowing for a reduction in strength and an increase in normalised slenderness at high temperatures. | 4.2.3.2 |
| The buckling reduction factor fi is the lower of its values about the yy and zz axes determined as in ambient-temperature design, except that the normalised slenderness used is adapted to the fire situation as follows: |  |
| - A special buckling curve for the fire situation is used, based on the slenderness at the critical temperature; - The buckling length lfi is determined as shown in Figure 13, provided that each storey of the building comprises a separate fire compartment, and that the fire resistance of the compartment boundaries is not less than that of the column. Because the continuing columns are much stiffer than the column in the fire compartment it is assumed that they cause the end(s) of the heated column to be restrained in rotation, so the effective length factor is taken as 0,5 for intermediate storeys and 0,7 for the top storey. |  |
| - Buckling lengths of columns in fire |  |
| - The relative slenderness of the column for the maximum temperature is given by: |  |
| - Fire resistance time of unprotected steel members |  |
| This is the time taken for a member to reach its critical temperature when subjected to a fire temperature curve. It is clearly necessary to be able to calculate the temperature development in any member in a simulated fire environment. The heat transfer to the member is predominantly by two mechanisms; radiation and convection. Since the rate of heating by both mechanisms is dependent at any time on the temperatures of both the fire atmosphere and the member, member temperature is related to time via a fairly complex differential equation. This is dealt with in Eurocode 3 by linearising the temperature increments over small time steps, which is impractical for hand calculation, but is ideal for setting up in software (a spreadsheet software for example). | Part 1-2 4.2.5.1 |
| For an unprotected steel section the temperature increase a,t in a small time interval t is given by the net amount of heat which the section acquires during this time: |  |
| with: |  |
| ca specific heat of steel a density of steel ksh a correction factor for the shadow effect, equal to 1,0 for convex hollow sections Am / V a “Section Factor” composed of Am exposed surface area of member per unit length V volume of member per unit length hnet,d design value of net heat flux per unit area |  |
| The net heat flux is composed of radiative and convective components, of which the radiative is: | EC1 Part 1-2 3.1 |
| in which, apart from the Stefan-Boltzmann constant of 5,6710-8 W/m2K4, |  |
|  is a configuration factor (can be set to 1,0 in the absence of data) res = f m is a resultant emissivity = emissivity of fire compartment  emissivity of member surface (1,0  0,8 = 0,8 if no specific data, 1,0  0,7 = 0,7 for carbon steel) r, m is the environment and member surface temperatures |  |
| and the convective heat flux is: |  |
| in which: |  |
| c is the convective heat transfer coefficient (subject to NAD values, but 25 W/m2°K used for Standard or External Fire curves, 50 W/m2°K for Hydrocarbon Fire) g, m is the environment (gas) and member surface temperatures | EC1 Part 1-2 3.2 |
| When forming the net heat flux from these each may be factored in order to account for differences in national practice in fire testing, but usually they are simply added together. |  |
| The “Section Factor” Am / V uses the exposed perimeter in calculating an appropriate value of Am and this means the actual surface which is exposed to radiation and convection. The principle is illustrated in the three examples given in Figure 14. |  |
| - Section factor calculation principles. | Part 1-2 Tables 4.2 |
| For hollow sections exposed on all sides, the section factor Am / V can be approximated by 1 / t. |  |
| - Fire resistance times of protected steel members |  |
| For members with passive protection the basic mechanisms of heat transfer are identical to those for unprotected steelwork, but the surface covering of material of very low conductivity induces a considerable reduction in the heating rate of the steel section. Also, the insulating layer itself has the capacity to store a certain amount of heat. It is acceptable to assume that the exposed insulation surface is at the fire atmosphere temperature. The calculation of steel temperature rise a.t in a time increment t is now concerned with balancing the heat conduction from the exposed surface with the heat stored in the insulation layer and the steel section: |  |
| but | Part 1-2 4.2.5.2 |
| in which the relative heat storage in the protection material is given by the term |  |
| with: |  |
| Ap / V section factor for protected steel member, where Ap is generally the inner perimeter of the protection material (except when there is a gap between the steel member and the protection) ca, cp specific heats of steel and protection material dp thickness of fire protection material a,t, g,t temperatures of steel and furnace gas at time t g,t increase of gas temperature during the time step t p thermal conductivity of the fire protection material a, p densities of steel and fire protection material | Part 1-2 Tables 4.3 |
| Fire protection materials often contain a certain percentage of moisture which evaporates at about 100°C, with considerable absorption of latent heat. This causes a “dwell” in the heating curve for a protected steel member at about this temperature while the water content is expelled from the protection layer. The incremental time-temperature relationship above does not model this effect, but this is at least a conservative approach. A method of calculating the dwell time is given, if required, in the ECCS Design Manual for Fire Saftety [7]. |  |
| - Use of advanced calculation models |  |
| Both Eurocodes 3 and 4 also permit the use of advanced calculation models based upon fundamental physical behaviour, which give a realistic analysis of the behaviour in fire of the structure. They may be used to represent the behaviour of individual members, the whole structure or sub-assemblies. All computational methods are to some extent approximate, are based on different assumptions, and are not all capable of predicting all possible types of behaviour. It is therefore stipulated that the validity of any such model used in design analysis must be agreed by the client, the designer and the competent building control authority. | Part 1-2 4.3 |
| Computational models may cover the thermal response of the structure to any defined fire, either nominal or parametric, and should not only be based on the established physical principles of heat transfer but should also on known variation of thermal material properties with temperature. The more advanced models may consider non-uniform thermal exposure, and heat transfer to adjacent structure. Since the influence of moisture content in protection materials is inevitably an additional safety feature it is permitted to neglect this in analysis. |  |
| When modelling the mechanical response of structures, the analysis must be based on acknowledged principles of structural mechanics, given the change of material properties with temperature. Thermally induced strains and their effects due to temperature increase and differentials must be included. Geometric non-linearity is essential when modelling in a domain of very high structural deflections, as is material non-linearity when stress-strain curves are highly curvilinear. It is, however, acknowledged that within the time-scale of accidental fires transient thermal creep does not need to be explicitly included provided that the elevated-temperature stress-strain curves given in the Code are used. This assumption may perhaps be revisited in the cooling phase of natural fires. |  |

| - Eurocode simple fire resistance calculation examples |  |
| --- | --- |
| - Design example |  |
| The following example is essentially of academic nature. It has been chosen not for resemblance to an existing structure but because it allows demonstrating the utilisation of different equations. It is a simple 4-storey frame, with bracing against horizontal sway deflection. Identical frames at 6 m spacing. |  |
| - Design example plane frame |  |
| Characteristic floor loadings: |  |
| - Permanent Gk = 1,9 kN/m2 - Primary Variable Qk,1 = 3,8 kN/m2 |  |
| Design Loads on Beams: |  |
| - Using G = 1,35 and Q,1 = 1,50 - Permanent actions Gd = 15,39 kN/m - Variable actions Qd = 34,2 kN/m |  |
| Steel grade: S275 used throughout. Composite elements will not be considered here. |  |
| - Fire Resistance and Protection of a Tension Member |  |
| - Tension member BE. |  |
| - Ambient temperature design of BE | Part 1-1 6.2.3 |
| Design Loading NEd = 247,95 kN |  |
| Required section |  |
| Anet = Npl,Rd / (fy / M0) = 247950 / (275 / 1,0) = 902 mm2 |  |
| Section: CHS 88,94, A = 1067 mm2 |  |
| - Fire resistance of tension member BE |  |
| Combination factor 1,1 = 0,5 | Part 1-2 |
| Design loading in fire Nfi,d = 1,0  57 + 0,5  114 = 114 kN | 2.4.2.1 |
| Design Resistance in Fire |  |
| Calculate resistance according to fire design, at ambient temperature: |  |
| Nfi,20,Rd = 1067  275 = 293,43 kN |  |
| Critical Temperature: | Part 1-2 |
| Degree of utilisation 0 = Nfi,d / Nfi,20,Rd = 114 / 293,43 = 0,39 | 4.2.3.1 |
| Critical temperature cr = 624°C | 4.2.4 (2) |
| Fire Resistance Time: |  |
| The change of steel temperature in time t is: |  |
| a,t = 1 / (ca a) (Am / V) hnet,d t |  |
| where: | 4.2.5.1 |
| Section factor Am / V: surface area of member / volume of member |  |
| Am / V = 0,279 / 1067 E-6 = 261 m-1 | Table 4.2 |
| Design value of net heat flux per unit area, hnet,d is determined for the Standard Fire, using f = 1,0 and m = 0,7. |  |
| By calculation using spreadsheet: | Part 1-2 2.2 (2) |
| For t = 5 seconds the time taken for the steel to reach its critical temperature is 10 minutes and 55 seconds. |  |
| - Fire protection of tension member BE | 4.2.5.2 |
| We require 60 minutes fire protection for the tension member. |  |
| Try an hypothetical protection material with the following characteristics: |  |
| Thickness dp = 20 mm Density p = 100 kg/m3 Specific heat cp = 1700 J/kg°K Thermal conductivity p = 0,092 W/m°K Section factor Ap / V = Am / V = 261 m-1 | Table 4.3 |
| Temperature increase of steel member in time t is: |  |
| a,t = (p / (dp ca a)) (Ap / V) [1 / (1 +  / 3)] (g,t - a,t) t - (e / 10 - 1) g,t | 4.2.5.2 |
| but a,t > 0. |  |
| where: |  |
| Gas temperature g,t is determined for the Standard Fire. Using spreadsheet and neglecting the contribution of the specific heat of the insulating material ( ≈ 0), after 60 minutes the steel temperature a = 520°C < 624°C (the critical temperature). |  |
| Therefore 20 mm protection provides more than 60 minutes fire protection. |  |
| - Fire Resistance and Protection of a Steel Beam | Part 1-2 |
| - Ambient temperature design of minor beam AB | 4.2.3.3 |
| - Minor beam AB |  |
| Applied bending moment MEd = 49,59  52 / 8 = 154,97 kNm |  |
| Try RHS 25015012, assuming that the design is controlled by strength and not by deflections. |  |
| Section Classification in the fire situation: |  |
| Coefficient  = (235 / fy)0,5 = 0,92 |  |
| Compression flange: c / t = (150 – 3  12) / 12 = 9,5 < 0,85  33  0,92 = 25,80 | Part 1-1 |
| Web: c / t = (250 – 3  12) / 12 = 17,8 < 0,85  72  0,92 = 56,3 | Table 5.2 |
| The section is therefore Class 1. |  |
| Moment Resistance: |  |
| The concrete floor slab provides full lateral restraint to the top flange, hence no need to consider lateral-torsional buckling. |  |
| Bending resistance: |  |
| Mpl.Rd = Wpl,y fy / M0 = 658.000  0,275 / (1,0  103) = 180,95 kNm > 154,97 |  |
|  Satisfactory |  |
| Shear Resistance: |  |
| Applied shear: VEd = 123,97 kN |  |
| Shear area: Av = 6000 mm2 |  |
| Shear capacity: Vpl,Rd = 6000  0,275 / (1,732  1,0) = 953 kN > 123,97 kN |  |
|  Satisfactory |  |
| - Fire resistance of minor beam AB |  |
| Design Loading in Fire: |  |
| Combination factor 1,1 = 0,5 | Part 1-2 |
| Design loading in fire: Mfi,d = (1,9 + 0,5  3,8) 6  52 / 8 = 71,25 kNm | 2.4.2 (1) |
| Design Resistance in Fire: |  |
| For a Class 1 beam with a uniform temperature distribution: |  |
| Design resistance in fire at time t = 0: |  |
| Mfi,t,Rd = Mfi,,Rd / 1 2 | 4.2.3.3 |
| For beam supporting concrete slab: |  |
| 1 = 0,7 and 2 = 1,0 |  |
| Mfi,0,Rd = 658.000  275 / (0,7  1,0) = 258,5 kNm |  |
| Critical Temperature: |  |
| Degree of utilization: 0 = 71,25 / 258,5 = 0,276 |  |
| Critical temperature: cr = 676 °C | 4.2.4 (2) or 4.2.4 |
| Fire Resistance Time: | Table 4.1 |
| The change of steel temperature in time t is: |  |
| a,t = (1 / (ca a)) (Am / V) hnet,d t |  |
| Where (for 3-sided exposure): |  |
| Section factor: |  |
| Am / V = surface area of member / volume of member = 0,65 / 0,00841 = 72,3 m-1 |  |
| Design value of net heat flux per unit area hnet,d is determined for the Standard Fire, using f = 1,0 and m = 0,7. |  |
| By calculation using spreadsheet: |  |
| For t = 5 seconds the time taken for the steel to reach its critical temperature is 23 minutes and 40 seconds. |  |
| - Fire protection of minor beam AB |  |
| We require 60 minutes fire protection for the minor beam. |  |
| Try encasing with 10 mm of hypothetical material: |  |
| Temperature increase of steel member in time t is: |  |
| a,t = (p / (dp ca a)) (Ap / V) [1 / (1 +  / 3)] (g,t - a,t)  - (e / 10 - 1) g,t | 4.2.5.2 |
| but a,t > 0. |  |
| Where: |  |
| Thickness dp = 10 mm Density p = 100 kg/m3 Specific heat cp = 1700 J/kg°K Thermal conductivity p = 0,277 W/m°K Section factor: Ap / V = Am / V = 72,3 m-1 | Table 4.3 |
| Gas temperature g,t is determined for the standard fire. |  |
| Using spreadsheet: |  |
| After 60 minutes the steel temperature a = 650°C < 676 °C (the critical temperature). | 4.2.5.2 |
| Therefore 10 mm thickness of insulation provides more than 60 minutes fire protection. |  |
| - Fire Resistance and Protection of a Steel Column | Part 1-2 4.2.3.2 |
| - Column GH |  |

| - Ambient temperature design of column GH |  |
| --- | --- |
| Axial compression, NEd = 991,8 kN |  |
| Section: RHS 15015012 |  |
| Section Classification in the fire situation: | Part 1-1 |
| Coefficient  = (235 / fy)0,5 = 0,92 | Table 5.2 |
| c / tw = (150 – 3  12) / 12 = 9,5 < 33  0,92  0,85 = 25,81 |  |
| The section is therefore Class 1. |  |
| Compression Resistance: |  |
| Slenderness  = 3,5 / 0,0544 = 64,3 |  |
| 1 = 86,8 |  |
| Normalised slenderness =  / 1 = 0,74 |  |
| Reduction factor (curve c for cold formed sections),  = 0,70 |  |
| A = 1 for Class 1 sections |  |
| M1 = 1,0 |  |
| Buckling resistance Nb.Rd =  A A fy / M1 = 1157 kN > 991,8 kN |  |
|  Satisfactory |  |
| - Fire resistance of steel column GH |  |
| - Buckling length (lowest storey) |  |
| Design Loading in Fire: | Part 1-2 |
| Design loading in fire: Nfi,d = (1,9 + 0,5  3,8) 5  6  4 = 456 kN | 2.4.2 (1) |
| Design Resistance in Fire: |  |
| Buckling resistance in fire: Nb,fi,t,Rd = fi A ky,max fy / M,fi |  |
| Effective length factor = 0,7 for lowest storey with pinned base. Intermediate storey would have 0,5. |  |
| Slenderness  = 45 |  |
| FIRST ITERATION |  |
| Assume that 1 in the fire situation = 0,85  86,8 = 73,78 | 4.2.3.2 |
| Normalised slenderness in the fire situation =  / 1 = 0,61 |  |
| Reduction factor in fire, fi = 0,67 |  |
| Nb,fi,0,Rd = 0,67  6100  1  0,275 / 1,0 = 1124 kN |  |
| Critical Temperature: |  |
| Degree of utilization, 0 = 456 / 1124 = 0,406 | Part 1-2 |
| Critical temperature cr = 617°C | 4.2.4 (2) or |
| KE = 0,279 | Table 4.1 |
| Kfy = 0,210 |  |
| (0,210 /0,279)0,5 = 0,868 | Part 1-2 Table 3.1 |
| SECOND ITERATION |  |
| 1 in the fire situation = 0,868  86,8 = 75,34 |  |
|  / 1 = 45 / 75,34 = 0,597 |  |
| Reduction factor in fire fi = 0,679 | Part 1-2 4.2.3.2 (2) |
| Nb,fi,0,Rd = 0,679  6100  1  0,275 / 1 = 1139 kN |  |
| Degree of utilization, 0 = 456 / 1139 = 0,400 |  |
| Critical temperature cr = 620°C ≈ 617°C |  |
| Note: Working in the load domain, that means calculating the load bearing capacity in the fire situation after a certain required time, e.g. 30 minutes, would not imply any iteration. |  |
| Fire Resistance Time: |  |
| The change of steel temperature in time t is: |  |
| a,t = (1 / (ca a)) (Am / V) hnet,d t |  |
| Where (for 4-sided exposure): |  |
| Section factor: Am / V = surface area of member / volume of member = 99,83 m-1 |  |
| By calculation using spreadsheet: |  |
| For t = 5 seconds the time taken for the steel to reach its critical temperature is 17 minutes and 12 seconds. |  |

- References

- EN 1991-1: Eurocode 1: Basis of Design and Actions on Structures. Part 1: Basis of Design.

- EN 1991-1-2: Eurocode 1: Basis of Design and Actions on Structures. Part 1.2: Actions on Structures Exposed to Fire.

- EN 1993-1-1: Eurocode 3: Design of Steel Structures. Part 1.1: General Rules: General Rules and Rules for Buildings.

- EN 1993-1-2: Eurocode 3: Design of Steel Structures. Part 1.2: General Rules: Structural Fire Design.

- EN 1994-1-1: Eurocode 4: Design of Composite Steel and Concrete Structures. Part 1.1: General Rules: General Rules and Rules for Buildings.

- EN 1994-1-2: Eurocode 4: Design of Composite Steel and Concrete Structures. Part 1.2: General Rules: Structural Fire Design.

- ECCS (1985). Design Manual on the European Recommendations for the Fire Safety of Steel Structures, European Convention for Constructional Steelwork, Brussels, Belgium.